## Sheet1
Gradient sampler wiring diagram
Device	Channel		Color	CR3000 Port	Ext. conn.
Trace gas analyzer analog outputs (0-5Vdc)	__________	signal		DF 1 H
		reference		DF 1 L
	__________	signal		DF 2 H
		reference		DF 2 L
	__________	signal		DF 3 H
		reference		DF 3 L
	__________	signal		DF 4 H
		reference		DF 4 L
BOTTOM level / aspirated thermistor / (Model 107; CSI)	Temp.	signal	red	SE 14
		reference	purple	earth
	Voltage excitation		black	VX3
	Shield		clear	earth
MIDDLE level / aspirated thermistor / (Model 107; CSI)	Temp.	signal	red	SE 15
		reference	purple	earth
	Voltage excitation		black	VX3
	Shield		clear	earth
TOP level / aspirated thermistor / (Model 107; CSI)	Temp.	signal	red	SE 16
		reference	purple	earth
	Voltage excitation		black	VX3
	Shield		clear	earth
Closed-path CO2/H2O analyzer	CO2	signal		DF 5 H
		reference		DF 5 L
	H2O	signal		DF 6 H
		reference		DF 6 L
PLUS EITHER:
Open-path CO2/H2O / analyzer / (LI-7500; Licor)	SDM	data	gray	C1
		clock	blue	C2
		enable	brown	C3
		ground	black	G
		shield	white	G
	Power (+)		red/white		12 V
Sonic anemometer / (CSAT3; CSI)	Power (-)		green		G
AND
Sonic anemometer / (CSAT3; CSI)	SDM	data	green	C1
		clock	white	C2
		enable	brown	C3
		ground	black	G
		shield	clear	G
	Power (+)		red		12 V
	Power (-)		black		G
OR
Sonic anemometer/ / open-path IRGA combo / (EC150+CSAT3A; CSI)	SDM	data	green	C1
		clock	white	C2
		enable	red	C3
		ground	black	G
		shield	clear	G
	Power (+)		red		12 V
	Power (-)		black		G
Reserved